### Ultimate capacity of reinforced concrete shear wall under

seismic excitation

D. Stefanov

Central Laboratory for Seismic Mechanics and Earthquake Engineering, Bulgarian Academy of Sciences, Acad.G.Bonchev str. Bl.3, Sofia 1113, Bulgaria, e-mail: seismech@geophys.bas.bg

Abstract. The seismic response of a reinforced concrete shear wall is investigated, taking into account the nonlinear behaviour of the materials – steel and concrete. Parametric and comparative investigations are done on the influence of the main   mechanical   characteristics of the materials on the structure capacity. The analytical and experimental results are compared in order to evaluate different factors, affecting the precision of the numerical solutions. A procedure for evaluation of ultimate capacity of shear walls under seismic excitations is proposed. The new procedure gives the possibility to get a good evaluation for failure mechanism of the investigated structure.

Key words:  nonlinear seismic behavior, cracked concrete, seismic response.

# 1.  Introduction

The evaluation of the seismic response of the reinforced concrete (RC) shear walls is of great importance in the seismic assessment of some building structures in nuclear power plants. That is because the shear walls are the main bearing elements, used to resist to seismic excitation. A typical example in this aspect is the reactor building structure, where the reactors VVER-1000 are located in NPP “Kozloduy”.

The subject of this analytical study is the seismic response and evaluation of the ultimate capacity of the reinforced concrete shear wall, tested dynamically on the shaking table.

The Organization for Economic Cooperation and Development (OECD) has organized a benchmark international project for response and ultimate capacity assessments of seismic RC shear walls. The experimental data [OECD/NEA&NUPEC 1994] kindly presented from the Nuclear Power Engineering Corporation of Japan (NUPEC) were used for this purpose. The experimental project “Elastoplastic test for reactor buildings” had the aim to create and modify the computer codes, as well as to improve the reliability of the methods for evaluation of the seismic stability. Part of the Japan project is carrying out of a large-scale dynamic test of RC shear walls on the shaking table.

Double T-shaped walls are located between two stiff slabs (story slabs). The thickness of the web wall is 75 mm and of the flange walls 100 mm. The clear height of the wall is 2020 mm. The length of the web is 3000 mm between the flange walls centers. The length of the flanges is 2980 mm. This shape of the test specimen is chosen with the purpose to model the situation in the real reactor building and to demonstrate the resistance of the specimen to horizontal shear seismic forces in the web plane.

2.  Preliminary investigations

The results of investigations, performed with a two-dimensional model of the tested wall, are summarized in [Stefanov 1997]. The modeling of the material reinforced concrete is made with two types of finite elements. The first one reflects the work of the concrete and the second one - the steel. The nonlinear properties of the concrete are expressed by the so called material constitutive law, giving the nonlinear relationship between the stresses and strains. An elastic-plastic stress-strain diagram is assumed for the steel. The analysis is performed with the computer code SOLVIA. The model of the concrete used is known as a model of Ottosen [SOLVIA 1992].

2.1  Monotonic quasi-static nonlinear analysis

The monotonic quasi-static nonlinear analysis is applied in cases when it is necessary to evaluate the ultimate capacity and the rigidity at various load levels. To derive the relationship between the lateral load and deformations (or displacements), the finite element model is loaded by separate steps and  the static solution is derived for each increment.  The loading can be in the form of lateral forces or displacements and continues stepwise until some failure occurs.

2.2  Cyclic quasi-static analysis with alternating loading

The loading function represents the maximum horizontal acceleration recorded at the top slab. It is an increasing cyclic alternating loading which is applied in the positive direction (conventionally called so) and after that applied in the negative direction with the same intensity. Each loading level from the experiment (RUN) is represented by one cycle, consisting of one positive and one negative branch up to the maximum load (acceleration). The whole loading function consists of 6 cycles. The stress-strain state achieved after each run is considered as an initial condition for the next run.

3. Parametric and comparative investigations of the influence of the main   mechanical   characteristics of the materials on the structure capacity

The preliminary investigations are expanded in order to evaluate the influence of the main mechanical characteristics of the materials on the structure capacity. Numerical experiments are performed and the parameters, which are varied, are the initial value of elastic modulus E0  and the tensile strength t of the concrete. During dynamic excitations, as the seismic ones are, these characteristics vary significantly in comparison with their static values (E0=23.4E+3 MPa,   t =2.28 MPa). Some calculation models are investigated, grouped in Table 1. In the first group – models M2G1 to M2G5, the aim is to investigate the influence of the tensile strength of the concrete, whereas the elastic modulus is constant. In the second group – models M2E2, M2E3 and M2E5, the two parameters are varied simultaneously. In the third group – models M3G1, M3G3 and M3G5, the values of the tensile strength of the concrete are again varied, but with an increased effective flange width.

Table 1.  Characteristics of the mathematical models

| Model | E0 Initial modulus of elasticity for concrete | t Tensile strength of the concrete | Effective flange width |
| --- | --- | --- | --- |
|  | MPa | MPa | m |
| M2G1 | 23.4E3 | 2.28 | 0.5 |
| M2G2 | 23.4E3 | 2.85 | 0.5 |
| M2G3 | 23.4E3 | 3.42 | 0.5 |
| M2G4 | 23.4E3 | 3.99 | 0.5 |
| M2G5 | 23.4E3 | 4.56 | 0.5 |
| M2E2 | 29.2E3 | 2.85 | 0.5 |
| M2E3 | 35.1E3 | 3.42 | 0.5 |
| M2E5 | 46.8E3 | 4.56 | 0.5 |
| M3G1 | 23.4E3 | 2.28 | 1.5 |
| M3G3 | 23.4E3 | 3.42 | 1.5 |
| M3G5 | 23.4E3 | 4.56 | 1.5 |

The derived results from the cyclic quasi-static nonlinear analysis, for concrete status and crack distribution, make it possible to draw conclusions about the failure mechanism with different models.

The comparison of the results from investigated models from the first group - M2G1, M2G2 to M2G5 lead to the following conclusions about the influence of the parameter tensile strength t of the concrete:

- Regarding the failure mechanism, the parameter t has significant influence. It is expressed in changing of the places where cracks concentration and failure due to concrete crushing are located. The results of model M2G3  (t = 3.42MPa) are the closest to the experimental ones. The maximum response values are summarized in Table 2. The deformed scheme and the crack distribution in the concrete at the last moment of the numerical solution are given in fig.1. As a whole the failure from concrete crushing is observed in the lower part of the web in the central area and near the flanges. The results derived concerning the last two models M2G4 and M2G5 – fig.2,  give grounds to conclude that increasing of the tensile strength of the concrete (two times the static) leads to the fact that cracks and failures are concentrated in the lowest part of the web, which is not in good agreement with the experimental behaviour of the specimen.

Table 2  Model M2G3, maximum response values

| Time | Vibration step RUN N | Input horizontal acceleration | Inertia force | Top slab horizontal displacement; Deformation angle |  | Vertical displacement of lower surface of top slab Left flange; Right flange |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | (mm/s2) | (MN) | Node 8 (mm) | (1/1000rad) | Node 162 (mm) | Node 6 (mm) |
| 1 | 1 | 2080 | .254 | .3569 | .1767 | -.1922 | -.4302 |
| 3 |  |  |  | -.3557 | -.1761 | -.4301 | -.1927 |
| 5 | 2 | 3980 | .485 | .6829 | .3381 | -.0841 | -.5396 |
| 7 |  |  |  | -.6813 | -.3373 | -.5395 | -.0847 |
| 9 | 2’ | 6070 | .741 | 1.0580 | .5238 | .0454 | -.6635 |
| 11 |  |  |  | -1.0368 | -.5133 | -.6527 | .0391 |
| 13 | 3 | 7040 | .859 | 1.4078 | .6969 | .2345 | -.7677 |
| 15 |  |  |  | -1.2695 | -.6285 | -.7184 | .1464 |
| 17 | 4 | 8820 | 1.076 | 2.2592 | 1.1184 | .6786 | -.9537 |
| 18.7 |  |  |  | -1.3369 | -.6618 | -.8461 | -.0003 |

- Regarding the ultimate capacity, the influence of the parameter  t is expressed in increasing  the capacity. In fig.3 is shown a comparison of the relationship “inertia load – horizontal displacement” (at the top slab) for models of the first group as well as the experimental results.

- The increasing of the concrete tensile strength (in comparison with the static value) leads to overestimation of the structure stiffness. Working with the static value of the tensile strength – both the ultimate capacity and the stiffness are underestimated. Therefore the acceptance of a given value of the tensile strength of

Fig.1  Deformed scheme and crack normals distribution at the last moment from  the numerical solution – model M2G3

Fig.2 Deformed scheme and crack normals distribution at the last moment from the numerical solution – model M2G5

Inertia load (MN)

Displacement (mm)

Fig.3 Relationship inertia load (MN) – horizontal displacement (cm) at first group  – models M2G1, M2G2 to M2G5

the concrete under dynamic excitation is a complicated question, having no single answer. Each case should be approached concretely  depending on the investigated structure and the aim of the analysis.

- From a calculating point of view it can be said that regarding the numerical solution the parameter t has no significant influence, but still at the models with higher values of the tensile strength of the concrete, the numerical solution is more stable.

The influence of the parameter elastic modulus of the concrete E0 can be seen from the results of the second group – models M2E2, M2E3 and M2E5:

- Regarding the failure mechanism it can be assumed that the increasing of E0  (together with t ) has little influence. In the case of model M2E2 crushing of the concrete can be seen in those parts which are in the middle of the web and a little bit above it. In the model M2E5 the bigger part of the concrete failure is concentrated in the lower web part – fig.4.

- Regarding the ultimate capacity, the results are similar to these from the first group. The comparisons are illustrated in fig.5.

- The parameter which has varied more significantly is the ultimate value of the horizontal displacements. Whereas at the model M2E2 the maximum displacement is 1.51 cm, at the model M2E5 it is 3.42 cm.

- At the model M2E5 a bigger calculating capacity of 1.277 MN is reached, in comparison with the other models. The failures from the concrete crushing in the lower part of the web and crack distribution in the other part, coincide relatively well with the experimental results.

As a whole it is clear that the results from model M2E5 are closer to the experimental results and the numerical solution is more stable in comparison with the other models.

The increased effective flange width at the models of the third group M3G1, M3G3 and M3G5 reflects on the failure mechanism, the crushed concrete areas being not in the lowest part of the web but are located a little bit higher.

Regarding the relationships inertia load – horizontal displacement, shown in fig.6, the results of model M3G3 are in good agreement with the test results.

The maximum calculated ultimate capacity, from all models, appears at model M3G5 and is equal to 1.309 MN, but the stiffness is overestimated, the corresponding maximum displacements are reduced and the failure nature is different from the test.

The analyzed RC wall has the capacity for shear forces of 1.3 MN, according to the Bulgarian “Codes for design of concrete and reinforced concrete structure, Sofia, 1988”. According  to  the  test   results the ultimate capacity  of  the

Fig.4  Deformed scheme and crack normals distribution at the last moment from the numerical solution – model M2E5

Fig.5 Relationship inertia load (MN) – horizontal displacement (cm) at second group – models M2E2, M2E3 to M2E5

wall is of 1.6 MN. The comparison of these results shows a good evaluation based on the existing code.

4. Procedure for evaluation of ultimate capacity for RC walls

Based on the investigations carried out and the conclusions drawn a following procedure can be suggested, the main points in which are:

- Modeling

At this preliminary stage a mathematical model of the structure must be chosen or developed, which reflects the structure adequately and models the dynamic behaviour with enough precision.

The application of the two dimensional models gives relatively good results with big reduction of computing time and resources. The finite element meshes do not need to be very refined, but to allow the displacements and deformations, corresponding to the anticipated failure mechanism – for example shear at walls with a relatively small height.

The steel reinforcement is modeled in two manners in principle. At the first one the available reinforcement is distributed uniformly where the corresponding equivalent depth is determined. This manner has the advantage that the finite element mesh is independent  of the real reinforcement location.  For these areas where there is a change in reinforcement the corresponding equivalent depth is changed. At the second manner a discrete location of linear finite elements is applied. In principle this manner is more complicated and requires to consider the finite element mesh with real location of steel bars. The advantage of this manner is the possibility to take into account the structure reinforcement  precisely, near “one by one” if the required computer resources are available.

- Consideration of the seismic excitation

For evaluation of the ultimate capacity a monotonic increasing loading and a quasi-static nonlinear analysis could be applied. As a result the relationship lateral force – displacement is derived for the structure or the different element under investigation. The advantages of this approach are simplicity and  rapidity and valuable information is derived for maximum capacity under horizontal loading.

A cyclic alternating loading and a quasi-static nonlinear analysis are applied in cases, when the evaluation of the whole system behaviour and failure mechanism is looked for.  By applying such a loading at different acceleration levels a dynamic character of real seismic excitations is imitated to a great extent. Additionally there is a possibility for a suitable acceleration scaling depending on a given seismic intensity of the region.

- Material properties

The nonlinear properties of concrete and steel are modeled by the so called material constitutive relationships, which gives the nonlinear relation between the stresses and strains at different stress states.

A hysteretic behaviour is observed under dynamic loading, describing the cycles of loading and unloading. Different models exist for a concrete work with a various shape of relationships ( - ), description of the hysteretic rules, as well as the way for taking into account the special features such as shear stiffness degradation and reduction factors of cracked concrete.

The professional computer codes can be divided into two groups. The first one consists of the so called codes for general use like ADINA, SOLVIA, ABACUS and the given constitutive laws are incorporated with criteria for cracking in concrete and criteria for tensile failure and crushing from compression. The second group consists of special codes for the nonlinear analysis. Typical subroutines are conducted to model the material properties, based on the experimental results for different structural elements (ABACUS, DYANA).

- Methods for nonlinear problem solution

The choice  of method for solution depends on the nonlinear strain level and time needed for the numerical solution. The modified-Newton method is suitable for the mean strain level and is less time consuming (per iteration). The BFGS method is usually effective but the full Newton method is most powerful, which is much time consuming. The line search algorithm helps in achieving convergence but also adds to the cost per iteration. However, the more expensive method (per iteration) may require less iterations to achieve convergence and finally to turn out less time consuming.

The procedure described is applied on the model, which has the same geometry and material properties like model M2G5. In fig.7 a function of uniformly increasing cyclic inertia loading is shown. The intensity of acceleration increases by 0.1g from one cycle to another. At a quasi-static nonlinear analysis the numerical solution stops at time t=37.20 s with the corresponding inertia loading of 1.22 MN. The horizontal displacement of the top slab is shown in fig.8. The deformed scheme and crack distribution at the last moment of the numerical solution are given in fig.9.

The comparison of the derived results (the deformed scheme, the status of the concrete and crack distribution) with the experimental ones, allows to conclude that the described procedure enables to get a good evaluation of the failure mechanism of the investigated structure.

5. Conclusion

Based on the investigations reported conclusions and recommendations can be generalized as follows:

1. A procedure for a deterministic evaluation of ultimate capacity of shear walls under seismic excitations is proposed. The new procedure gives the possibility to get a good evaluation of the investigated structure. The broad area of applicability is ensured by using the cyclic alternating inertia loading. It gives the chance to imitate, to a great extent, the main characteristics of the seismic excitations. The main advantage is expressed in the reduction of computer resources

Fig.6 Relationship inertia load (MN) – horizontal displacement (cm) at third group – models M3G1, M3G3 and M3G5

Fig.7 Function of uniformly increasing alternating loading (acceleration)

(memory, disk space and time) and avoiding the necessity of performing the time history analysis.

2. Based on the above investigations the following recommendations can be drawn for the application of nonlinear analyses of the shear walls at the evaluation of the seismic stability of the important structures:

Fig.8 Horizontal displacement of the top slab – model M2-A5

Fig.9 Deformed scheme and crack normals distribution at the last moment from the numerical solution – model M2-A5

- The monotonic quasi-static nonlinear analysis can be recommended for determination of the ultimate capacity for structures with bearing walls for lateral loading. The numerical results coincide with these from the  experiment;

- The cyclic quasi-static nonlinear analysis can be recommended for investigation of the failure mechanism of the treated structure and the whole response of the system under excitations similar to seismic one.

- The cyclic alternating loading gives the possibility to follow the process of appearance (first crack) and distribution of the cracks in the concrete.

3. The ultimate capacity value for analyzed reinforced concrete shear wall indicates an approximately 20% higher value than the ultimate value calculated according to the Bulgarian code. This is an additional margin which has to account for the evaluation of the existing buildings and facilities in the nuclear power plants regarding their seismic qualification.

References

OECD/NEA&NUPEC 1994, Specification Report of Seismic Shear Wall ISP on NUPEC’s Seismic Ultimate Dynamic Response Test.

Stefanov D., Nonlinear behaviour of reinforced concrete shear wall under seismic excitation, 8th National Congress on Theoretical and Applied Mechanics, Sofia, 1997.

SOLVIA 90-2, Computer code for stress analyses, User Manual, Solvia Engineering, 1992.

#### Граничен капацитет на стоманобетонна стена при сеизмично въздействие

Д. Стефанов

Резюме.  Изследвано е сеизмичното реагиране на стоманобетонна стена с отчитане на нелинейното поведение на материалите – стомана и бетон. Проведени са параметрични и сравнителни изследвания на влиянието на основните механични характеристики на материалите върху капацитета на изследваната конструкция. Направени са сравнения на аналитично получените с експерименталните резултати с оглед оценка на различните фактори, влияещи върху точността на числените решения. Предложена е методика за оценка  на  граничния  капацитет на стоманобетонни стени при сеизмични въздействия. Новата методика дава възможност да се получи и една добра оценка на механизма на разрушение на изследваната конструкция.